RACK PULL BATTERY ASSEMBLY

Design Review Summary

COTS Passive Assembly  ·  480–576 VDC  ·  400 kW  ·  12-String Interface

# 1. What This Assembly Is

The Rack Pull Battery Assembly is a commercially manufactured (COTS), purely passive electrical interconnect assembly. It contains no active electronics, no control logic, and no software. Its function is to provide a rated, protected, and properly interfaced connection point between the lithium-ion battery racks and the Power Distribution Rack (PDR).

| Parameter | Value |
| --- | --- |
| Assembly type | COTS — Commercial Off The Shelf |
| Function | Passive interconnect — batteries to PDR |
| DC voltage range | 480 VDC minimum to 576 VDC maximum |
| Discharge power capacity | 400 kW |
| String interfaces | 12 parallel battery string connections |
| Protection devices | 1500A Bussmann fuses (one per string) |
| Battery cable connections | 12 × 300 kcmil (one per string) |
| PDR output connections | 2 × 350 kcmil per bus bar |
| Bus bars | Common positive bus and common negative bus |
| Ground bus | Tied to facility ground — single point bond |

# 2. Scope of Responsibility

Because this is a COTS product, the design team's responsibility is limited to verifying correct application — not internal design. The following table defines what is and is not in scope.

| In Scope (Application) | Out of Scope (Manufacturer Design) |
| --- | --- |
| Voltage range compatibility | Internal fuse selection methodology |
| Current rating adequacy | Bus bar material and cross-section design |
| Interface compatibility — cable sizes and connectors | Enclosure structural calculations |
| Correct installation — weight, clearances, torque | Component-level fault current calculations |
| Coordination with upstream protection | Internal wiring and termination design |
| Ground bus tie to facility ground | Product listing and certification basis |

Key Statement: If a reviewer asks about internal design decisions — fuse sizing methodology, bus bar cross-section calculation, or internal wiring — the correct answer is: 'That is a manufacturer design decision. The product is listed for this application. I can provide the manufacturer datasheet and contact.'

# 3. System Context — Where This Assembly Sits

The Rack Pull Battery Assembly is not an isolated component. It sits within a defined upstream protection stack. Understanding this stack is essential to answering coordination questions at the design review.

UPSTREAM PROTECTION STACK ───────────────────────────────────────────────────────── UTILITY (12 kV) ↓ MAIN TRANSFORMER 500 kVA, 12kV → 480/277V, 3-Phase, 4-Wire 4.5% Impedance, ±2.5% primary and secondary taps ↓ SERVICE DISCONNECT SWITCH 800A, 480/277V, 3-Phase, 4-Wire ↓ TEMPEST FILTER 800A ↓ IFS MAIN CIRCUIT BREAKER 800AF / 800AS, 480/277V, 3-Phase, 4-Wire ↓ IFS CIRCUIT BREAKER 600AF / 600AS ↓ [DC RECTIFIER / CHARGER] ↓ RACK PULL BATTERY ASSEMBLY ← THIS ASSEMBLY 1500A Bussmann Fuse per string Common (+) and (–) Bus Bars ↓ PDR (Power Distribution Rack) ─────────────────────────────────────────────────────────

# 4. Available Fault Current — Key Calculation

The transformer is the limiting source of fault current on the AC side. This number is important for understanding the upstream breaker coordination and confirming the fuse interrupt rating is adequate.

TRANSFORMER FAULT CURRENT CALCULATION ───────────────────────────────────────────────────────── Transformer rating: 500 kVA Secondary voltage: 480V Impedance (Z%): 4.5% Available fault current (Isc): Isc = kVA ÷ (√3 × V × Z%) Isc = 500,000 ÷ (1.732 × 480 × 0.045) Isc = 500,000 ÷ 37.3 Isc ≈ 13,400A at transformer secondary ───────────────────────────────────────────────────────── This is the maximum fault current the upstream breakers (800A, 600A) must coordinate against.

Critical Distinction: The 1500A Bussmann fuses protect against inter-string fault current — which is battery-sourced and independent of the transformer. These are two separate fault current sources. The upstream AC breakers coordinate against transformer fault current (~13,400A). The string fuses coordinate against battery inter-string fault current. Do not confuse the two.

# 5. Load Current Analysis

The following calculations confirm the assembly is correctly rated for the application.

DISCHARGE CURRENT CALCULATIONS ───────────────────────────────────────────────────────── Maximum discharge current (at minimum voltage): 400 kW ÷ 480 VDC = 833A total Minimum discharge current (at maximum voltage): 400 kW ÷ 576 VDC = 694A total Per string (12 strings): 833A ÷ 12 = ~69A continuous per string Fuse ratio: 1500A fuse protecting ~69A continuous = 21× continuous → Fuse is NOT sized for continuous current → Fuse IS sized for inter-string fault current ─────────────────────────────────────────────────────────

# 6. The 1500A Bussmann Fuses — How They Work

This is the question reviewers are most likely to ask. The fuses do not protect the strings against overload — they protect against inter-string fault current from the parallel battery bank.

## Why 1500A for a 69A Continuous Load?

When one battery string develops a fault, all 11 remaining strings drive current through that string's fuse. This inter-string fault current can be many thousands of amperes — far above the 69A continuous per-string current. The 1500A fuse is sized to interrupt this fault current, not the continuous load current.

## How the Fuse Curve Works

| Current Multiple | Approximate Current | Fuse Behavior |
| --- | --- | --- |
| 1.0× (continuous) | 1,500A | Fuse remains closed — this is continuous rating |
| 1.5× | 2,250A | Opens in minutes — overload region |
| 3× | 4,500A | Opens in seconds |
| 10× | 15,000A | Opens in milliseconds |
| 20×+ | 30,000A+ | Current limiting — clips fault peak in <1ms |

At inter-string fault current levels (potentially 10,000–30,000A depending on string impedance), the fuse operates in the current-limiting region — it opens so fast it actually reduces the peak fault current before it reaches maximum.

# 7. Cable Notation — How to Read It

Cable specifications follow a standard notation. Here is how to read the PDR cable specification:

PDR OUTPUT CABLE SPECIFICATION: 2-(4-1/C #500 + 1/C #2 GND) 2 = 2 conduit runs 4 = 4 conductors per conduit 1/C = single conductor (one wire per run) #500 = 500 kcmil conductor size +1/C #2 = plus one conductor, #2 AWG GND = ground conductor SAY OUT LOUD: 'Two conduit runs, each containing four single-conductor 500 kcmil cables plus one number two AWG ground.'

| Connection | Specification | Purpose |
| --- | --- | --- |
| Battery strings (each) | 300 kcmil | 12 string inputs to assembly |
| PDR output | 2 × (4 × 500 kcmil + #2 GND) | Assembly output to PDR bus bars |
| Ground bus | Tied to facility ground | Single-point protective earth bond |

# 8. Protection Coordination Summary

The three-sentence answer that covers coordination at the design review:

Coordination Answer: The 1500A Bussmann fuses are sized to interrupt inter-string fault current from the parallel battery bank — not the continuous load current. At fault levels, they operate in the current-limiting region, clearing before the upstream IFS DC breaker reaches its trip threshold. The transformer and IFS are upstream backup — they coordinate against the ~13,400A transformer-available fault current and do not operate for string-level battery faults.

COORDINATION HIERARCHY ───────────────────────────────────────────────────────── DEVICE RATING FAULT SOURCE ROLE ───────────────────────────────────────────────────────── IFS Main CB 800AS Transformer AC Upstream backup IFS CB 600AS Transformer AC Backup 1500A Fuses >>13.4kA Battery DC First to clear (inter-string) on string fault ───────────────────────────────────────────────────────── Fuse clears FASTER than breaker at high fault current. Breaker handles lower-level sustained faults from AC side. Two independent fault current sources — do not conflate.

# 9. Likely Review Questions and Answers

| Question | Your Answer |
| --- | --- |
| Why 1500A fuse for a 69A string? | Fuse is sized for inter-string fault current, not continuous load. When one string faults, 11 strings drive current through that fuse. |
| Is the fuse DC rated at 576V? | Yes — Bussmann [part number] is DC rated. Datasheet available. |
| What is the interrupt rating? | Manufacturer specified — exceeds available fault current. Datasheet available. |
| Walk me through a string fault. | String faults → 11 strings drive current through fuse → fuse opens in current-limiting region → fault cleared before upstream breaker trips. |
| How does it coordinate with the IFS breaker? | Fuse clears faster than IFS at battery fault current levels. IFS sees transformer-limited current, not battery inter-string current. |
| What is the available fault current? | ~13,400A from transformer at 4.5% Z. Battery inter-string fault current is separate and higher. |
| Why those cable sizes? | Manufacturer selection for the rated application. Product is COTS — cable sizing is a manufacturer design decision. |
| What's the bus bar ampacity? | Manufacturer rated for the application at 400kW/833A. Datasheet available. |
| Who is responsible for the internal design? | The manufacturer. My responsibility is correct application selection — voltage, current, and interface compatibility. |

# 10. What to Bring to the Review

- Manufacturer datasheet / schematic — the primary artifact

- This summary document

- Single-line diagram showing assembly in system context

- The three key numbers: 833A max current, 576V max voltage, ~13,400A transformer fault current

- One-sentence scope statement ready: 'This is a COTS product — my responsibility is correct application selection.'

Bottom Line: You are integrating a COTS product — not designing one. Know that it fits the voltage, the current, and the interfaces. Know why the fuse is 1500A. Know the upstream fault current number. Redirect everything else to the datasheet and the manufacturer.

— End of Summary —