QTS PDU Factory Witness Test Procedure

Transformer Impedance & Functional Verification

Unit Under Test:

| Transformer Rating: | 500 kVA, K-4, Dry-Type | Serial #: _________ |
| --- | --- | --- |
| Input Voltage: | 480 VAC ± 15%, 3-phase, 3-wire + ground | Job #: _________ |
| Output Voltage: | 480/277V, 400/230V, or 208/120 VAC (multi-tap) | Date: _________ |
| Nominal Impedance: | 7.5% (minimum 4.5% per manufacturer tolerance) | Witness: _________ |
| Voltage Taps: | 6 taps at 2.5% increments (2 above, 4 below nominal) |  |

1. Purpose

1.1 To perform routine transformer tests and PDU functional verification per IEEE C57.12.91 and IEEE C57.12.01.

1.2 To verify minimum 7.5% short-circuit impedance at each voltage tap.

2. Reference Standards

2.1 IEEE C57.12.01 - General Requirements for Dry-Type Distribution and Power Transformers

2.2 IEEE C57.12.91 - Test Code for Dry-Type Distribution and Power Transformers

2.3 IEEE C57.12.59 - Guide for Dry-Type Transformer Through-Fault Current Duration

3. Test Equipment

3.1 Pacific Power Supplies (2 units in parallel configuration)

3.2 Step-Down Transformer (480V/600V input to 208V output)

3.3 True RMS Multimeter (calibrated within 12 months)

3.4 Clamp Meter (0-1000A, True RMS)

3.5 Power Analyzer

3.6 Insulation Resistance Tester (Megger, 1000 VDC)

3.7 Thermal Imager

4. Test Setup

4.1 Test Circuit Configuration:

50A Circuit → Pacific Power (A, B, C, N, G) → Step-Down Transformer → DUT (QTS PDU)

4.2 Pacific Power Supply Settings (Low Voltage / High Current Mode):

4.2.1 Verify both Pacific Power units are connected in parallel.

4.2.2 Set to Low Voltage Range.

4.2.3 Set Maximum Current Limit to ~600A.

4.2.4 Slowly ramp up voltage until target current is reached.

4.3 Step-Down Transformer:

4.3.1 Input: 480V or 600V from Pacific Power supplies.

4.3.2 Output: 208V to DUT high-voltage input (A, B, C).

4.4 DUT Connections:

4.4.1 Connect step-down transformer output to PDU HV input terminals (A, B, C).

4.4.2 PDU LV output terminals (A, B, C, N) to be configured per test requirements.

5. Initial Inspection

5.1 Verify all test equipment has been calibrated within the last 12 months.

5.2 Review the job order form and verify unit is configured as described.

5.3 Verify nameplate data matches one-line diagram and specification.

5.4 Verify the Input Color Code: A phase - Brown, B phase - Orange, C phase - Yellow.

5.5 Verify the Output Color Code: A phase - Black, B phase - Red, C phase - Blue.

5.6 Verify/record transformer thermostat states: Warning 180°C (N.O.), Shutdown 200°C (N.C.).

5.7 Verify all CB magnetic trips are set on high.

6. Transformer Routine Tests (per IEEE C57.12.91)

6.1 Winding Resistance Measurement

6.1.1 Measure and record primary winding resistance (phase-to-phase).

6.1.2 Measure and record secondary winding resistance (phase-to-phase and phase-to-neutral).

6.1.3 Record ambient temperature at time of measurement.

6.2 Turns Ratio Test

6.2.1 Measure turns ratio at each voltage tap position.

6.2.2 Verify ratio is within ±0.5% of nameplate.

6.3 Insulation Resistance Test

6.3.1 HV winding to LV winding: _______ MΩ @ 1000 VDC

6.3.2 HV winding to Ground: _______ MΩ @ 1000 VDC

6.3.3 LV winding to Ground: _______ MΩ @ 1000 VDC

6.3.4 Acceptance: ≥ 100 MΩ

7. Impedance Test at Each Voltage Tap (per IEEE C57.12.91 Clause 9)

Test Current: 600A (rated current for 500 kVA @ 480V)

Acceptance: Minimum 7.5% impedance (no less than 4.5% after tolerances)

7.1 Short-circuit the secondary (output) terminals.

7.2 Apply reduced voltage to primary until rated current (600A) flows.

7.3 Record applied voltage (Vsc), current (Isc), and power (Psc).

7.4 Calculate percent impedance: %Z = (Vsc / Vrated) × 100

7.5 Repeat test at each voltage tap and record in table below.

| Tap Position | Tap Voltage | Vsc (V) | Isc (A) | %Z | Pass/Fail |
| --- | --- | --- | --- | --- | --- |
| +2 (+5%) | 504V |  |  |  |  |
| +1 (+2.5%) | 492V |  |  |  |  |
| Nominal | 480V |  |  |  |  |
| -1 (-2.5%) | 468V |  |  |  |  |
| -2 (-5%) | 456V |  |  |  |  |
| -3 (-7.5%) | 444V |  |  |  |  |
| -4 (-10%) | 432V |  |  |  |  |

Ambient Temperature: _______ °C

8. Dielectric Withstand Test (Hipot)

8.1 Open Surge Suppressor Fuses.

8.2 Disconnect DC Connectors from control boards.

8.3 Disconnect three-phase connectors from VVIT Board.

8.4 Disconnect GND lug from GND Bus bar.

8.5 Close all Circuit Breakers.

8.6 Jump together input phases. Hipot Voltage = (input V × 2) + 1000 = _______ V

8.7 Jump together output phases. Hipot Voltage = (output V × 2) + 1000 = _______ V

8.8 Apply test voltage for 60 seconds.

8.9 Acceptance: No breakdown/arc, tester PASS, leakage ≤ programmed limit.

9. PDU Functional Tests

9.1 Voltage Verification

9.1.1 Verify Input Voltages across F1, F2, F3 fuses.

9.1.2 Verify Output Voltages across F7, F8, F9 fuses.

9.1.3 Reconnect DC and three phase connectors.

9.2 Phase Rotation

9.2.1 Using a phase rotation meter, verify rotation is A, B, C at input and each distribution breaker.

9.2.2 To verify phase rotation alarm: Turn off power, swap input phases B and C, apply power, verify alarm.

9.2.3 Turn off power and swap phases back to correct position.

9.3 Alarm/Fault Testing

9.3.1 Trip sub feed breakers one at a time; verify three alarms appear (two auxiliary NO, NC and one bell).

9.3.2 Completely open the tripped breaker, verify bell alarm goes away.

9.3.3 Close the previously tripped breaker, verify both auxiliary alarms go away.

9.3.4 Repeat for all sub feed breakers.

9.4 Remote Emergency Power Off (REPO)

9.4.1 Pull REPO connector from VVIT board, short with a jumper.

9.4.2 Verify main breaker trips and alarms appear.

9.4.3 Reset main breaker.

9.5 Transformer Temperature Alarms

9.5.1 Pull THERM connector from VVIT board, short with a jumper.

9.5.2 Verify main breaker trips and alarms appear.

9.5.3 Reset main breaker.

9.6 EPO Button

9.6.1 Press EPO on the outside of the unit.

9.6.2 Verify main breaker trips and alarms appear.

9.6.3 Reset main breaker.

9.7 Phase Loss/Low Voltage Alarm

9.7.1 Remove input phase C fuse and verify input BC and CA phase loss alarm.

9.7.2 Remove output phase A fuse and verify output L-AB, L-AC, L-AN low voltage alarm.

9.7.3 Reinstall all fuses.

9.8 Monitor Calibration Verification

9.8.1 Measure each parameter with multimeter and compare to monitor display.

9.8.2 Monitor shall be within ±2% of actual readings (per spec accuracy requirements).

9.8.3 Verify: Input V (L-L), Output V (L-L), Output V (L-N), Output current, Ground current.

9.9 Communications

9.9.1 Connect ethernet cable to monitor, configure PC IP address to unit IP ±1.

9.9.2 Verify web interface connectivity.

9.9.3 SNMP: Open MIB browser, walk the unit, verify PDU values appear.

10. Thermal Scan

10.1 After minimum 30 minutes at load, use thermal camera to scan transformer and connections.

10.2 Acceptance: No connection temperature rise > 30°C above ambient or > 60°C absolute.

11. Discrepancies

11.1 Record all discrepancies below:

_____________________________________________________________________________

_____________________________________________________________________________

_____________________________________________________________________________

12. Witness Sign-Off

12.1 Review completed test data with witness.

12.2 Obtain witness signature on test report.

Test Technician: _________________________ Date: _____________

Witness: _________________________ Date: _____________

Engineering (if deviations): _________________________ Date: _____________